## Electromagnetics
Topic | Description | Question Text | Option A | Option B | Option C | Option D | Correct Answer
Electromagnetics | Computation | Calculate the capacitance of a parallel plate capacitor having 20 cm x 20 cm square pates separated by a distance of 1 mm. Assume the dielectric medium to be air with permittivity of 8.85 x10^-12 F/m. | 354 microFarad | 354 picoFArad | 3.54 microFarad | 3.54 picoFarad | B
Electromagnetics | Computation | Two capacitors are in series are charged cross a 24 V source. If C1 is 12 pF and the voltage across is 6 , find the C2. | 6 pF | 8 pF | 2 pF | 4 pF | D
Electromagnetics | Computation | In a 12 V battery supplies 10 A, find the amount of energy in kJ delivered in one hour. | 120 | 216 | 324 | 432 | D
Electromagnetics | Computation | A flux of 13.6 mWb penetrates a coil of wire 240 mm in diameter. Find the magnitude of the magnetic flux density in Tesla if the plane of the coil is perpendicular to the field. | 0.3 | 0.8 | 0.4 | 0.5 | A
Electromagnetics | Computation | Two similar poles, each of 1 Wb, placed 1 m apart in air will experience a repulsive force of _______ | 63 kN | 796 N | 8 TN | 63 mN | A
Electromagnetics | Computation | When one coil of a magnetically coupled pair has a current of 7.0 A, the resulting flux 1 and 2 are 0.50 mWb, and 0.75 mWb, respectively. What is the coefficient of coupling K, if the number of turns N1 and N2 are 100 and 300, respectively? | 0.4 | 0.8 | 0.2 | 0.6 | D
Electromagnetics | Computation | A straight conductor 100 cm long and carrying a current of 40 A lies perpendicular to a magnetic field of 1.5 Wb/m^2. What is the mechanical power in watt/s required to move the conductor at a uniform speed of 6 m/s ? | 390 W | 300 W | 330 W | 360 W | B
Electromagnetics | Objective | A good example of kinetic energy is provided by ________. | a tornado | a wound clock spring | an automobile storage battery | the raised weights of grandfather’s clock | A
Electromagnetics | Objective | The condition of a liquid electrolyte is measured in terms of its | current value | specific gravity | acid content | voltage output | B
Electromagnetics | Objective | Residual magnetism is necessary in a | separately excited generator | self – excited generator | both of these | none of these | B
Electromagnetics | Objective | In case of delta connected circuit, when one resistor is open, power will be | unaltered | reduced to 1/9 | reduced to 1/16 | reduced by 1/3 | D
Electromagnetics | Objective | The specific gravity of a lead-acid cell is often used as a measure of its ________________ | rate of discharge | operating temperature | state of charge | life expectancy | C

## Electrical Circuits 1
Topic | Description | Question Text | Option A | Option B | Option C | Option D | Correct Answer
Electrical Circuits 1 | Computation | What is the total resistance of the eleven 33 k-ohm resistors in parallel? | 33 k-ohm | 3 k-ohm | 363 k-ohm | 11 k-ohm | B
Electrical Circuits 1 | Computation | A 15 – ohm resistor is connected in parallel with a series combination of resistors of 8 and 12 ohms. If the drop across the 8-ohm resistor is 48 V, determine the total current? | 16 | 18 | 20 | 22 | A
Electrical Circuits 1 | Computation | How many 100 k-ohm will be connected in parallel to obtain 20 k-ohm? | 8 | 6 | 5 | 4 | C
Electrical Circuits 1 | Computation | Find the maximum power that can be drawn from a 12 V battery if its internal resistance is 0.25 ohm. | 72 W | 144 W | 576 W | 36 W | B
Electrical Circuits 1 | Computation | A resistance of 6 ohms is connected in parallel with another resistor across a 120 V supply. The total current taken from the supply was found to be 40 A. What is the value of resistance R. | 1 ohm | 2 ohms | 4 ohms | 6 ohms | D
Electrical Circuits 1 | Computation | Three resistors A,B and C are connected in series to a 120 V supply. If the resistor A = 60 ohms and the voltage across resistor B = 40 V when the current is ½ A, what is the resistance of resistor C in ohms? | 105 | 90 | 110 | 100 | D
Electrical Circuits 1 | Computation | The voltage applied across an electric press was reduced by 50%. The power consumed by the press will be reduced to | 25% | 50% | 60% | . 75% | A
Electrical Circuits 1 | Computation | Resistor 1 has twice the resistance of resistor 2. They are connected in parallel to a battery. Find the ratio of thermal energy generated in resistor 1 to that in resistor 2? | 2:1 | 1:4 | 4:1 | 1:2 | D
Electrical Circuits 1 | Computation | An equal number of electrons is placed on two metal spheres 3 cm apart in air. How many electrons are on each sphere if the resultant force is 4 kN? | 1.47 x 10^14 | 1.33 x 10^14 | 1.25 x 10^14 | 1.40 x 10^14 | C
Electrical Circuits 1 | Computation | An aluminum cable has an identical strands, a length of 1 500 m and a diameter of 2.50 mm each. What is the resistance of the cable? | 86.3 ohm | 0.863 ohm | 56.3 ohm | 0.563 ohm | B
Electrical Circuits 1 | Computation | Three resistor A, B, and C are connected in series to a 120 V supply. If the resistor A = 60 ohms and the voltage across resistor B = 40 V when the current is 0.5 A, what is the resistance of C in ohms? | 105 | 90 | 110 | 100 | D
Electrical Circuits 1 | Computation | A 36 ohm resistor is connected in parallel with an unknown resistor R. Their combination is then connected in series with a 12 ohm resistor. Find the value of R such that the power drawn by the parallel combination of 36 ohm and R is equal to the power in the 12 ohm resitor. | 6 ohm | 18 ohm | 24 ohm | 48 ohm | B
Electrical Circuits 1 | Computation | A dc ammeter has an internal resistance of 0.1 ohm. A shunt of 1.01 milli-ohm is connected to the ammeter. What is the multiplier of the set up? | 10 | 50 | 80 | 100 | D
Electrical Circuits 1 | Computation | A capacitor is charged with 0.01 C . If the energy stored is 1 joule, find the capacitance in microFarad. | 5 | 50 | 500 | 5 000 | B
Electrical Circuits 1 | Computation | If a certain conductor has an area of 336 400 CM, what is the radius of the conductor in cm? | 0.663 | 0.81 | 0.737 | 0.921 | C
Electrical Circuits 1 | Computation | Three resistances of 4.9, and 11 ohms are connected in series and then in parallel. Find the effective resistance for series connection. | 15 ohms | 20 ohms | 24 ohms | 13 ohms | C
Electrical Circuits 1 | Computation | Three resistors A, B, and C are connected in series to a 120-v supply. If the resistor A = 50 ohms and the voltage across resistor B = 40 v when the current is 1/2 A, what is the resistance of resistor C in ohms? | 105 | 90 | 110 | 100 | C
Electrical Circuits 1 | Computation | In a 12-v battery supplies 10 A, find the amount of energy in KJ delivered in one hour | 120 | 216 | 324 | 432 | D
Electrical Circuits 1 | Computation | The terminal voltage of a battery is 11.8 v when delivering 20 w of power to an external load resistor R. If the battery has an emf of 15 v, find the internal resistance of the battery. | 1.96 ohms | 1.89 ohms | 1.68 ohms | 1.75 ohms | B
Electrical Circuits 1 | Objective | The effect of electric shock in the human body will depend on | line voltage | line current | current flowing in the body | none of these | C
Electrical Circuits 1 | Objective | The resistance of the rod does NOT depend on | its temperature | its type of material | its length | the shape of its cross sectional area | A
Electrical Circuits 1 | Objective | The current is zero in a conductor when NO potential difference is applied because _____________. | the electrons are not moving fast enough | equal number of electrons and protons are moving together | the electrons are not moving | for every electron with a given velocity there is another with the velocity of equal magnitude and opposite in direction | D
Electrical Circuits 1 | Objective | The curve representing ohm’s law is | parabola | linear | a sine function | a hyperbola | B
Electrical Circuits 1 | Objective | The condition in Ohm’s Law is that | ratio V/I should be constant | current should be proportional to voltage | the temperature should remain constant | the temperature should vary | C
Electrical Circuits 1 | Objective | Inside a hollow spherical conductor | electric field is zero | electric field is constant | electric field changes with distance from the center of the sphere | electric field is unity | A
Electrical Circuits 1 | Objective | When the voltage remains the same, the current will _______________ as the impedance decrease I. decrease II. increase | I only | both | either I and II | II only | B
|  | When electrons build up pressure at one point, it is called _____________. | ganging | current flow | impedance | pressure filing | B

## Electrical Circuits 2
Topic | Description | Question Text | Option A | Option B | Option C | Option D | Correct Answer
Electrical Circuits 2 | Computation | A 6 ohm resistor is connected in series with an inductor L across a 110 V, 60 Hz source and draws a current of 10 A. Find L. | 23.5 mH | 24.5 mH | 25.5 mH | 26.5 mH | B
Electrical Circuits 2 | Computation | Find the average power absorbed by a balance three phase load in an ABC circuit in which V_CB = 208 angle 15 and I_B = 3 angle 110. | 1 080 W | 624 W | 358 W | 620 W | D
Electrical Circuits 2 | Computation | A symmetrical three-phase 240 V supply balance delta connected load of 6 – j8 per phase. What is the line current? | -25 + j32 | 25 - j5.78 | -25 - j32 | 25 + j32 | D
Electrical Circuits 2 | Computation | The current in a 4-H inductor decrease uniformly from 30 A to 10 A in 0.2s. What is the inductor voltage for this time? | 100 V | 200 V | 300 V | 400 V | D
Electrical Circuits 2 | Computation | Three 6.6 resistors are connected in wye. What is the equivalent of the delta connected resistors? | 2.22 ohms | 20 ohms | 11.54 ohms | 10 ohms | B
Electrical Circuits 2 | Computation | What is the total power consumed by the load when the reading of two wattmeters are 5 kW and -0.5 kW? | 5.5 kW | 4.5 kW | 5 kW | 4.05 kW | B
Electrical Circuits 2 | Computation | An inductive coil consumes active power of 500 W and draws 10 A from 60 Hz AC supply of 110 V. What is the coil inductance? | 26 mH | 28 mH | 30 mH | 32 mH | A
Electrical Circuits 2 | Computation | A delta 3-phase, 4 wire secondary 230/115 would have a high leg to neutral voltage of | 200 V | 208 V | 115 V | 230 V | A
Electrical Circuits 2 | Computation | When 3 A flows through a circuit with an input admittance of 0.4 + j0.5 S, what reactive power does the circuit consumed? | 11 VAR | -8.7 VAR | 8.7 VAR | -11 VAR | D
Electrical Circuits 2 | Computation | A coil of wire having a value of 10 + j16 ohms is connected in series with a capacitance reactance Xc, and this series combination is then connected in parallel with resistor R. If the equivalent impedance of the circuit is 8 + j0 ohm, what is the value of Xc? | 14 | 18 | 10 | 16 | D
Electrical Circuits 2 | Computation | A washing machine is in effect, an RL circuit. If the machine is rated 311 W and 4.5 A from 155 V source when operating normally. Find its power factor? | 0.75 lagging | 0.65 lagging | 0.70 lagging | 0.60 lagging | D
Electrical Circuits 2 | Computation | A single phase inductive load draws 10 MW at 60% lagging power factor. Determine the reactive power of a capacitor in MVAR to be connected in arallel with the load to raise the power factor to 85%. | 48 | 51 | 56 | 43 | C
Electrical Circuits 2 | Computation | A series connected circuit has R = 4 ohms and L = 25 mH. Calculate the value of C that will produce a quality factor of 50. | 62.5 microF | 6.25 microF | 0.625 microF | 25 microF | A
Electrical Circuits 2 | Computation | If 25 ohms and 125 A are the base impedance and base current, respectively for a given system, what is the base kVA? | 781.25 | 39.1 | 390.625 | 78.12 | C
Electrical Circuits 2 | Computation | A symmetrical three-phase 240 V supplies a balanced delta connected load of 6 – j8 ohms per phase. What is the line current? | -25 + j32 A | 25 – j5.78 A | -25 – j32 A | 25 + j32 | D
Electrical Circuits 2 | Computation | The rms value of pure cosine function is | 0.5 of peak value | 0.707 of peak value | same as peak value | zero | B
Electrical Circuits 2 | Computation | A coil having a resistance of 10 ohms and an inductance of 4 H is switched across a 20 V dc source. Calculate the rate of current change when the current reaches 50% of its final steady value? | 2.5 A/s | 3.5 A/s | 4.5 A/s | 5.5 A/s | A
Electrical Circuits 2 | Computation | To a series RLC circuit, a voltage of 10 V is applied. If Q of the coil at resonant frequency is 20, the voltage across the inductor at resonant frequency will be | 200 V | 100 V | 75 V | 50 V | A
Electrical Circuits 2 | Computation | In ACB sequence balanced three phase system, the angle between the line voltage and the line current is 50 degrees, what is the lagging power factor of the system? | 0.3 | 0.5 | 0.64 | 0.94 | D
Electrical Circuits 2 | Computation | In laboratory experiment, the impedance of a coil was obtained at 60Hz, and 30 Hz. These are 75.48 ohms and 57.44 ohms, respectively. What is the inductance of the coil? | 150 mH | 182.5 mH | 42.5 mH | 2.1 mH | A
Electrical Circuits 2 | Computation | A half wave rectified sine wave has an average value of 100 A. What is its effective value? | 157 A | 70.71 A | 100 A | 141.4 A | A
Electrical Circuits 2 | Computation | A coil of wire having a value of 10 + j16 ohms is connected in series with a capacitive reactance, and this series combination is then connected in parallel with a resistor R. If the equivalent impedance of the circuit is 8+j0 ohms, what is the value of capacitive reactance in ohms? | 18 | 10 | 16 | 5 | C
Electrical Circuits 2 | Computation | In a series RC circuit, the voltage across the capacitor and the resistor are 60 v and 80 v respectively. What is the total voltage of the circuit? | 120 V | 115 V | 100 V | 105 V | C
Electrical Circuits 2 | Computation | What is Vbn in this balance three-phase in which Van = 7200 cis 20 and Vcn =7200 cis -100? | 7200 cis -80 | 7200 cis 120 | 7200 cis 90 | 7200 cis 140 | D
Electrical Circuits 2 | Computation | Determine the circuit element and its value for V = 120 sin (377t - 30) volt and I = 4 sin (377t + 60) A. | Xc = 30 ohms and C = 66.31 microF | Xc = 40 ohms and C = 66.31 microF | Xc = 30 ohms and C = 88.42 microF | Xc = 40 ohms and C = 88.42 microF | C
Electrical Circuits 2 | Computation | A washing machine is, in effect, an RL circuit. If the machine takes 311 W and 4.5 A from a 115-v source when operating normally. Find its power factor. | 0.70 lagging | 0.80 lagging | 0.75 lagging | 0.60 lagging | D
Electrical Circuits 2 | Computation | The current in a series circuit R = 100 ohms and L= 60 mH lags the applied voltage by 80 degrees. What is the source frequency in Hz? | 144.3 | 163.5 | 150.4 | 174.6 | C
Electrical Circuits 2 | Computation | A 240 v, 3 phase, 3-wire system has two balanced 3 phase loads. Load I, delta connected takes 24 KW at 0.8 pf leading and load 2, wye-connected takes 20 KVA at 0.766 pf lagging. Find the line current in amperes | 88.6 | 110.4 | 92.8 | 95.4 | D
Electrical Circuits 2 | Objective | The electrical analog of a spring constant k is | L | 1/L | C | 1/C | D
Electrical Circuits 2 | Objective | An alternating current with a frequency of 60 Hz is passed through a moving coil galvanometer that measures DC current. What will the galvanometer reading be equal to? | the peak value of the AC current | the average value of the AC current | the rms value | a negligible current | D
Electrical Circuits 2 | Objective | Which of the following effects are generally less for an alternating current than for a direct current? | heating effects | chemical effects | magnetic effects | impedance | B
Electrical Circuits 2 | Objective | Which of the following AC device is used to measure the angle between the voltage and its current? | reactive meter | power factor meter | demand meter | phase angle meter | D
Electrical Circuits 2 | Objective | When the amplitude of the oscillator in a series RLC circuit is doubled the ________. | current amplitude is doubled | the voltage across the capacitor is halved | impedance is doubled | capacitor reactance is halved | A
Electrical Circuits 2 | Objective | An LC series circuit with an inductance L and a capacitor C has an oscillation frequency of f. Two conductors, each with inductance L, and two capacitors, each with a capacitance C, are all wired in series and the circuit is completed. The oscillation frequency is __________. | f/4 | f | 2f | f/2 | B
Electrical Circuits 2 | Objective | The current flowing in L and C at parallel resonance are | zero | equal | infinite | different | B
Electrical Circuits 2 | Objective | A sine wave has a frequency of 60 Hz. Its angular frequency is | 120pi | 60pi | 30pi | 6pi | A
Electrical Circuits 2 | Objective | In a loss – free RLC circuit, the transient current is | oscillating | square wave | sinusoidal | non-oscillating | C

## Fund. of Electronics
Topic | Description | Question Text | Option A | Option B | Option C | Option D | Correct Answer
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | Find the frequency of the radio wave whose wavelength is 600 m. | 500 Hz | 500 kHz | 150 Hz | 150 kHz | B
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | Wavelength is a distance travelled by an electronic wave during the time of one cycle. Given a wavelength of 12 m, what is the frequency? | 250 kHz | 25 kHz | 250 MHz | 25 MHz | D
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | What is the maximum output power of a cellular transmitter? | 4.5 W | 1.5 W | 3 W | 6 W | C
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | Single side band signal produces a peak to peak voltage of 720 v on voice peaks across a 75-ohm antenna. What is the peak envelope power? | 865 W | 856 W | 835 W | 853 W | A
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | In full-wave rectification, if the input frequency is 60 Hz, then output has a frequency of ___________ | 30 Hz | 60 Hz | 120 Hz | 240 Hz | C
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | What is the maximum output power of the cellular transmitter? | 4.5 W | 1.5 W | 3W | 6 W | C
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | Impurities in an electrolyte can cause an internal short circuit condition called ______ | depolarization | polarization | electrolysis | local action | D
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | Cellular phones operate in the frequency range of | EHF | VHF | UHF | SHF | C
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | Find the frequency if radio wave whose wavelength is 600 m. | 500 Hz | 500 kHz | 150 Hz | 150 kHz | B
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | A type of electronics communication in which only one party transmits a time. | full duplex | half duplex | bicom | simplex | B
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | A transponder with a bandwidth of 400 MHz uses polarization diversity. If the wavelength allocated to transmit a single telephone channel is 4 kHz, how many telephone channels can be carried by the transponder? | 300 000 | 400 000 | 100 000 | 200 000 | D
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | The amplitude modulation generated at a very low voltage or power amplifier is ___________ modulation. | minimum | collector | high level | low level | D
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | Which of these is NOT a simplex type of electronic communication? | TV broadcasting | Facsimile or fax | Paging service | Telephone | D
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | In television system, channels 2 and 13 are classified as | VFH | UHF | SHF | EHF | A
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | Which of the following is a primary disadvantage of FM over AM? | Lower efficiency | Noise susceptibility | Higher cost and complexity | Excessive use of spectrum space | D
Fundamentals of Electronics Communication, Electronics 1 and 2 |  | Which of the following principle will the operation of fiber-optic cable is based? | dispersion | refraction | reflection | absorption | C

## Apparatus and Industrial Elec.
Topic | Description | Question Text | Option A | Option B | Option C | Option D | Correct Answer
Electrical Apparatus and Industrial Electronics | Computation | A three – phase wye – delta connected, 50 MVA, 345 / 34.5 kV transformer is protected by a differential protection is 150:5. What is the current on the secondary side of CT’s? | 3.83 A | 2.53 A | 4.50 A | 4.83 A | D
Electrical Apparatus and Industrial Electronics | Computation | A 13.8 kV/ 440, 50 kVA single phase transformer has a leakage reactance of 300 ohms referred to 13.8 kV side. Determine the per unit value of the leakage reactance for the low voltage base. | 0.305 | 0.04 | 0.097 | 0.079 | D
Electrical Apparatus and Industrial Electronics | Computation | Given a 100 kVA, 2 400/240 V single phase transformer. Find the current transformer (CT) ratio at the low voltage side. | 700:5 | 600:5 | 500:5 | 400:5 | C
Electrical Apparatus and Industrial Electronics | Computation | An ideal transformer 2 400/240 V has a certain load of 50 A, unity power factor which is to be connected to the low voltage winding. This load must have exactly 200 V across it. With 2400 applied to the high voltage winding, what resistance must be added in series with the transformer at the low voltage winding? | 0.9 ohm | 0.6 ohm | 0.8 ohm | . 0.7 ohm | C
Electrical Apparatus and Industrial Electronics | Computation | The overload kVA of each transformer of an open-delta bank is 11.55. If each transformer is rated 37.5 kVA, then what is the kVA of the balanced 3 phase load? | 70 | 80 | 85 | 90 | C
Electrical Apparatus and Industrial Electronics | Computation | A 7.5 MVA, 69/13.8 kV, 3 –phase transformer has 8% impedance. What is the per unit impedance at 10 MVA base? | 0.24 | 0.106 | 0.06 | 0.096 | B
Electrical Apparatus and Industrial Electronics | Computation | A transformer is rated 10 kVA, 440/110 V and 60 Hz when operated as a conventional 2 winding transformer. The transformer is to be used as a 550/440 V step down autotransformer in a distribution system. What is the new kVA rating of the transformer in this manner? | 20 | 10 | 37.5 | 50 | D
Electrical Apparatus and Industrial Electronics | Computation | What is the maximum flux in mWb of a transformer with 200 primary turns when connected to a 60 Hz, 200 V supply? | 10.35 | 6.25 | 50.5 | 3.75 | D
Electrical Apparatus and Industrial Electronics | Computation | A 500 kVA, 34.5/13.8 kV, 3 phase transformer is delta-wye connected. The primary and secondary winding resistances are 35 ohms and 0.876 ohm per phase, respectively. Calculate the percent efficiency. | 97.8 | 98.7 | 96.4 | 97.2 | B
Electrical Apparatus and Industrial Electronics | Computation | A 75 kVA, 13 200/240 V 60 Hz, single phase transformer has 1% resistance and 3% reactance. Find the the copper loss of the transformer at 3/4 of full load and unity power factor. | 185 W | 422 W | 368 W | 508 W | B
Electrical Apparatus and Industrial Electronics | Computation | In a transformer, the core loss is found to be 60 watts at 30 Hz and 90 watts at 40 Hz measured at the same maximum flux density. Compute the eddy current and hysteresis losses at 60 Hz in watts. | 90,75 | 85,60 | 95,69 | 88,72 | A
Electrical Apparatus and Industrial Electronics | Computation | A transformer rated at a maximum of 50 KVA supplies a 25-kW load at power factor 75% lagging. How many kW additional load may be added at unity power factor without exceeding the transformer rating? | 24 | 25 | 29 | 20 | D
Electrical Apparatus and Industrial Electronics | Computation | A transformer has a primary winding of 2000 turns and voltage of 2400 v and current of 8.66 - j5 with an impedance Z2 connected across the secondary winding. The secondary winding has 500 turns. What is the value of the secondary impedance? | 8.66 +j5 ohms | 26 + j15 ohms | 15.32 + j10 ohms | 13 + j7.5 ohms | D
Electrical Apparatus and Industrial Electronics | Objective | To protect the delta-delta power transformer against fault, CT will have _____ connection | delta – delta | delta – wye | wye-delta | wye-wye | D
Electrical Apparatus and Industrial Electronics | Objective | What protection is based on the comparison of current phasors I1 and I2 based on Kirchhoff’s current law? | distance protection | additional protection | differential protection | inferential | C
Electrical Apparatus and Industrial Electronics | Objective | A multi-meter is connected to one terminal of primary of a transformer and the other terminal to the secondary of the same transformer to measure the resistance. The multimeter reading would be | infinity | zero | equal to the resistance of the winding | zero or infinity | A
Electrical Apparatus and Industrial Electronics | Objective | The transformer oil used in transformers provides | cooling and lubrication | insulation and lubrication | insulation and cooling | insulation cooling and lubrication | C
Electrical Apparatus and Industrial Electronics | Objective | What is PEMC in EPIRA stands for ? | Philippine Energy Market Corporation | Philippine Electricity Market Corporation | Private Energy Marketing Company | Philippine Electrical Marketing Corporation | B
Electrical Apparatus and Industrial Electronics | Objective | The capacitors of the power factor are rated in terms of | kV | kW | kVA | kVAR | D
Electrical Apparatus and Industrial Electronics | Objective | What is the device function number of directional power relay? | 27 | 30 | 32 | 37 | C
Electrical Apparatus and Industrial Electronics | Objective | Which of the following transformer has only one winding? | current | distribution | autotransformer | power | C
Electrical Apparatus and Industrial Electronics | Objective | An ideal full wave rectifier with non-inductive load has zero transformation losses. What is the efficiency? | 70% | 80% | 90% | 100% | B
Electrical Apparatus and Industrial Electronics | Objective | The purpose of insulating oil when used on power circuit breaker are the following, EXCEPT; | Interrupter | Coolant | Insulation | Quencher | A
Electrical Apparatus and Industrial Electronics | Objective | This is the compact arrangement of switching devices; | circuit protector | switchboard | switchgear | panelboard | C
Electrical Apparatus and Industrial Electronics | Objective | The purpose of insulating oil when used on power circuit breaker are the following, EXCEPT; | Coolant | Interrupter | Quencher | Insulation | B

## Machine 1
Topic | Description | Question Text | Option A | Option B | Option C | Option D | Correct Answer
Electrical Machine 1 | Computation | Calculate the torque in N-m developed by a 440 V dc motor having an armature resistance of 0.25 ohm and running at 750 rpm when taking a current of 60A. | 240 | 325 | 285 | 342 | B
Electrical Machine 1 | Computation | How many commutator bars does a 6 pole dc generator with 4 coil elements per slot and 20 slots per pole has? | 60 | 120 | 240 | 480 | C
Electrical Machine 1 | Computation | A dc shunt motor develops 15 hp at 120 V. If the effective armature resistance is 0.061 ohm and the field winding draws 2 A, what is the overall efficiency? | 90% | 93% | 94% | 95% | B
Electrical Machine 1 | Computation | An 8 pole triplex wave wound armature carries a total of 660 A. If there are 8 brush arms, calculate the current in each armature conductor. | 110 A | 66 A | 22 A | 11:00 | A
Electrical Machine 1 | Computation | A generator delivers a load through a pair of wires, each of which has a resistance of 0. 06 ohm. If the load voltage and power are 120 v and 4.8 kW, respectively. what is the generated voltage? | 125.5 V | 126.8 V | 124.8 V | 123.5 V | C
Electrical Machine 1 | Computation | In a 4-pole, 60 Hz, 200v induction motor having a full-load current of 350 A, torque developed is 700 N-m. What is the approximate speed of the motor? | 1100 rpm | 955 rpm | 870 rpm | 1250 rpm | B
Electrical Machine 1 | Computation | A generator delivers a load through a pair of wires, each of which has a resistance of 0.06 ohm. If the load voltage and power are 120 v and 4.8 kW, respectively what is the power loss in the line wires? | 96 W | 198 W | 192 W | 99 W | C
Electrical Machine 1 | Objective | If the torque angle continuously increases, system will become | stable | unstable | oscillatory stable | asymptotic stable | B
Electrical Machine 1 | Objective | If the field of a dc shunt motor is opened | It will continue to run at its rated speed | The speed of the motor will become very high | The motor will stop | The speed of the motor will decrease | B
Electrical Machine 1 | Objective | The dummy coil in dc machine is used to | eliminate reactance voltage | eliminate armature reaction | bring about mechanical balance of armature | eliminate harmonics developed in the machine | C
Electrical Machine 1 | Objective | With reference to armature windings, wave windings are often called | cascade | series | parallel | ring | B
Electrical Machine 1 | Objective | What device is used to measure the temperature of the motor winding while the motor is in operation? | Seismic probe | Resistance temperature detector | Thermocouples | Proximity probe | B

## Machine 2
Topic | Description | Question Text | Option A | Option B | Option C | Option D | Correct Answer
Electrical Machine 2 | Computation | A 4 – pole induction motor running with 5% slip is supplied by a 60 Hz synchronous generator. Determine the speed of the motor. | 1 674 rpm | 1 728 rpm | 1 710 rpm | 1 827 rpm | C
Electrical Machine 2 | Computation | A 440 V, 70 HP shunt motor has an armature of 0.185 ohm and field resistance of 350 ohms. The current drawn by this machine is 135 A at full load. IF this machine is to deliver torque to 175% of that at full-load, what would be the resistance of its starters? | 3.4 ohm | 5.6 ohm | 2.2 ohm | 1.7 ohm | D
Electrical Machine 2 | Computation | An induction motor with 8 poles, 60 Hz is operated with a slip of 3%. Calculate the rotor speed. | 1684 | 1024 | 873 | 927 | C
Electrical Machine 2 | Computation | A 4 – pole wave wound generator has 220 coils of 10 turns each. The resistance of each turn is 0.02 ohm . Find the resistance of the armature winding? | 11 ohms | 22 ohms | 0.2 ohm | 0.44 ohm | A
Electrical Machine 2 | Computation | A 60 Hz, 4 pole, 3 phase induction motor has a slip of 2.5%. What is the slip speed in rpm? | 55 | 40 | 60 | 45 | D
Electrical Machine 2 | Computation | In a 15 hp, 460 Hz, 6 pole, 3 phase induction motor has a full load slip of 4%. Find the full load torque in N-m. | 85 | 88 | 93 | 90 | C
Electrical Machine 2 | Computation | A 440 V, 60 Hz, 6 pole, 3 phase induction motor has rotor input power of 33 kW at rated voltage and frequency. Under this condition, the rotor emf makes 126 complete cycles/minute. Find the rotor resistance in ohm/phase if the rotor current is 60 A/phase. | 0.0118 | 0.0107 | . 0.107 | 0.118 | C
Electrical Machine 2 | Computation | The starting current of a 15 hp, 460 V, 3 phase induction motor is 130 A. What voltage in volts should be applied to the motor so that the starting current will not exceed 84.8 A? | 238 | 295 | 300 | 310 | C
Electrical Machine 2 | Computation | The field system of a 50 Hz alternator has a sinusoidal flux per pole of 0.1 Wb. Calculate the emf generated in one turn which spans two-thirds of a pole pitch. | 17.4 V | 19.2 V | 12.2 V | 9.6 V | B
Electrical Machine 2 | Computation | Two compound generators are operated in parallel. If generator A has a series-field resistance of 0.0015 ohm and is adjusted to take 30% of the line load while generator B with a series field resistance of 0.001 ohm takes the remainder of the load, what is the current flow in the equalizer, when the load is 230 kW at 230 v? | 300 A | 100 A | 400 A | 200 A | C
Electrical Machine 2 | Computation | An induction motor draws 50 KW at a 0.60 lagging power factor from a 480 v, 60 Hz source. What parallel capacitor will increase the overall power factor to 0.90 lagging? | 532 microFarad | 489 microFarad | 704 microFarad | 582 microFarad | B
Electrical Machine 2 | Objective | Open circuit test on transformer is conducted to determine | hysteresis loss | copper loss | core loss | eddy current loss | C
Electrical Machine 2 | Objective | In a synchronous motor, the magnitude of the stator back emf depends on | load of the motor | dc excitation only | both the speed and rotor flux | none of these | B
Electrical Machine 2 | Objective | Alternators installed in a hydro power station, are of | low speed | high speed | medium speed | very high speed | C
Electrical Machine 2 | Objective | One of the advantages of distributing the winding in alternator is to | reduce harmonics | reduce the amount of copper | improve voltage waveform | decrease the value of the voltage | C
Electrical Machine 2 | Objective | To adjust the power of alternator, adjust the _____________ | power factor | governor | field current | frequency | B
Electrical Machine 2 | Objective | Copper loss of a transformer is determined by means of a/an ____________ test. | open circuit | polarity | short circuit | inductive circuit | C

## Instrumentation, Feedback, Rese
Topic | Description | Question Text | Option A | Option B | Option C | Option D | Correct Answer
Instrumentation & Control, Feedback Control System and Research Methods |  | Transient current in RLC circuit is oscillatory when | R = 0 | R =2 sqrt (L/C) | R > 2 sqrt (L/C) | R < 2 sqrt (L/C) | D
|  | What is the IEEE device function number 50? | AC time overcurrent relay | Instantaneous overcurrent relay | AC circuit breaker | Differential protective relay | B
|  | One primary and one secondary terminal of a two winding transformer are connected to an ohm meter instrument. What will be the reading on this instrument? | infinity | equal to winding resistance | zero or infinity | zero | A
|  | What is the equivalent IEEE device function number for distance relay? | 21 | 32 | 37 | 87 | A
|  | What is the equivalent IEEE device number for an under – voltage relay? | 67 | 52 | 27 | 51 | C
|  | The undervoltage relays are usually used for what protection of the electrical equipment? | feeder protection | motor protection | transformer protection | bus-bar protection | B

## Electrical System & Illum
Topic | Description | Question Text | Option A | Option B | Option C | Option D | Correct Answer
Electrical System and Illumination Engineering Design | Computation | A 120 W 240 V gas fitted lamp has a mean spherical candle power of 95. Find its efficiency in lumens per watt. | 9.95 | 5.99 | 9.59 | 8.99 | A
Electrical System and Illumination Engineering Design | Computation | A light source is located 2 m from a surface produces an illumination of 50 flux on that surface. Find the intensity of the light source in candela. | 100 | 50 | 150 | 200 | D
Electrical System and Illumination Engineering Design | Computation | A room air conditioner is to be attached to an individual branch circuit. If the load is 12 A, what is the minimum size of branch circuit is required? | 15 A | 13.8 A | 8.7 A | 9.6 A | A
Electrical System and Illumination Engineering Design | Computation | A 100 W 230 V gas lifted lamp has a mean spherical candle power of 92. Find the efficiency in lumens per watt. | 9.56 | 10.56 | 11.56 | 12.56 | C
Electrical System and Illumination Engineering Design | Computation | When installing two grounding electrodes, the minimum distance between them is | 1 800 mm | 2 000 mm | 1 500 mm | 2 400 mm | A
Electrical System and Illumination Engineering Design | Computation | What is the maximum plug and cord rating of a 30-A branch circuit? | 24 A | 30 A | 26 A | 28 A | A
Electrical System and Illumination Engineering Design | Computation | In a 13.8 kV, 10 MVA base three phase system, a phase to phase fault occurs. If the Thevenin’s equivalent impedance of the system is 2.63%, what is the per unit fault current? | 19.01 pu | 32.93 pu | 57.03 pu | 98.78 pu | B
Electrical System and Illumination Engineering Design | Computation | A light source located 2.75 m from a surface produces an illumination of 528 lux on that surface. Find the illumination if the distance is changed to 1.55 m. | 298 lux | 1 662 lux | 937 lux | 168 lux | B
Electrical System and Illumination Engineering Design | Computation | The current from neutral to ground connection is 12 A. What is the zero sequence component in phases? | 12 A | 36 A | 4 A | 3 A | C
Electrical System and Illumination Engineering Design | Computation | What is the total flux emitted of four lamps having an intensity of 100 Cd each? | 1,256 Im | 2,512 Im | 5,026 Im | 10,052 Im | C
Electrical System and Illumination Engineering Design | Objective | Which of the following type of fault used only the equivalent positive sequence impedance of the circuit in the short-circuit calculation? | line to line | line to ground | double line to ground | three phase fault | D
Electrical System and Illumination Engineering Design | Objective | RA 7832 concerns on ________________. | pilferage of electricity, theft of transmission materials and capping of system loss | pilferage of electricity, theft of transmission materials and rationalizing of system loss | pilferage of electrical energy | pilferage of electricity and electrical materials | B
Electrical System and Illumination Engineering Design | Objective | The overcurrent protective device is caused to operate by_________________. | Voltage Surge | Current Flow | Voltage Drop | Impedance | B
Electrical System and Illumination Engineering Design | Objective | What is the maximum quarter bends permitted in rigid conduits between outlets? | 4 quarter bends | 6 quarter bends | 2 quarter bends | 3 quarter bends | A
Electrical System and Illumination Engineering Design | Objective | Energy radiated continuously in the form of lighting waves is called | luminous intensity | lumen | luminous flux | illumination | C
Electrical System and Illumination Engineering Design | Objective | Which of these is not a factor in the selection of fuse rating for protection of a branch circuit? | Branch full-load current | System impedance | Branch fault-current | System voltage | B

## Power Plant & Dist.
Topic | Description | Question Text | Option A | Option B | Option C | Option D | Correct Answer
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Computation | At a 115 kV substation, PT ratio is 1000 and CT ration is 1200/5. The potential going into the wattmeter is 115 V. What is the M indicated when the wattmeter reads 800 W? | 150 MW | 192 MW | 15 MW | 19.2 MW | B
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Computation | A power plant gets water from a dam from a height of 122.45 m at the rate of 1 000 cubic meters per minute. If the output of the plant is 15 000 kW, what is the plant efficiency? | 80% | 75% | 70% | 65% | B
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Computation | Calculate the use factor of a power plant if the capacity factor is 35% as it operates 8 000 hrs during the year. | 38.32% | 33.82% | 36.82% | 32.54% | A
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Computation | A power station supplies 60 kW to a load over 2 500 ft of 000 2 – conductor copper feeder resistance of which is 0.078 ohm per 1000 ft. The bus bar voltage is maintained constant at 600 V. Determine the maximum power which can be transmitted. | 60 kW | 230.7 kW | 120 kW | 150 kW | B
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Computation | A wind generator with an efficiency of 80% has a blade diameter of 20 m. If the wind velocity is 30 km/hr, how much power in kW is obtained from the generator? | 58.47 | 45.78 | 48.75 | 54.87 | D
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Computation | In a certain are, the energy consumption is expected to double in 10 years. Assuming a simple exponential growth given by P = Poe^at, what is the growth rate? | 6.39% | 5.39% | 6.93% | 5.93% | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Computation | A small wind generator is designed to generate 75 kW of power at a wind velocity of 30 mi/hr. What is the approximate blade diameter of the wind generator in ft? | 35.4 | 31.9 | 33.6 | 37.3 | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Computation | A hydroelectric power plant consumes 60 x 106 kWh per year. What is the net head if the expected flow is 1,500 cubic meter per minute and overall efficiency of 63%? | 33.3 m | 44.3 m | 55.3 m | 66.3 m | B
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | Power plant having the maximum efficiency is | thermal | hydro | diesel | nuclear | D
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | In a certain country, the equivalent fuel reserve of power generator is 3 x 10^6 MW-years. The present peak power demand is 200 GW, and the expected power consumption growth rate is 2.1 percent. How long will the fuel reserve last? | 8 years | 11 years | 13 years | 14 years | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | Which of the following is not included in the evaluation of Technical Performance of Distribution System according to the Philippine Distribution Code (PDC)? | Power Quality | Reliability | Collecting Efficiency | System Efficiency | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | A distributor is designed from the point of view of | voltage drop | current carrying capacity | voltage drop and current carrying capacity | load capacity | A
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | The type of AC distribution system commonly used to supply both light and power is the | open delta system | three phase delta system | three-phase wye system with neutral wire | three phase wye system without neutral wire | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | When a power plant is not able to meet the demand of the consumers it will resort to | load shedding | efficient plant operation | power factor improvement at the generators | penalizing high load consumers by increasing the charges of electricity | A
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | Based load plants are designed to supply power at ________________. | low capital cost and low operating cost | high capital cost and low operating costs | low capital cost an high operating cost | high capital cost and high operating cost | B
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | Which of the following define the meaning of load factor? | The ratio of average load to the installed capacity | The ratio of maximum load to average load | The ratio of average load to maximum load | The ratio of connected load to maximum load. | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | A common utility’s tariff practice to penalize industrial consumers whose power factor falls below _______ and give incentive for power factor above ________. | 80%, 90% | 75%, 90% | 85%, 85% | 75%,85% | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | In a transformers | high tension winding is used in the transformer | high tension winding is used away from the core | low tension winding is used near the core | low tension winding is used away from the core | A
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | Which of the following shall be included in the calculation of the reliability standard indices of the distributor asset by the Philippine Distribution Code? | Outages that occur on the secondary lines of the distribution system | Planned outages where the customer have been notified at least three (3) days prior to the loss of power. | Outages that occur on the primary lines of the distribution system. | Outages that occur in the transmission line. | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | Peak load plants are designed to supply power at _______. | low capital cost and low operating cost | high capital cost and low operating cost | low capital cost and high operating cost | high capital cost and high operating cost | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | Which of the following methods of generating electric power from the sea water is more advantageous? | water power | ocean power | tidal power | none of these | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | What does PEMC in EPIRA stands for? | Philippine Energy Market Corporation | Private Energy Marketing Company | Philippine Electricity Market Corporation | Philippine Electrical Marketing Corporation | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | Which of the following power plant is conventional source of energy? | Solar Energy | Geothermal | Coal Energy | Wind Energy | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | PDC in EPIRA means | Philippine Distribution Commission | Philippine Distribution Code | Philippine Distribution Corporation | Philippine Distribution Company | B
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | Efficiency is secondary consideration in case of | base load plants | peak load plants | both (a) and (b) | none of these | B
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | Which plant takes the least time in starting from cold conditions to full load operation? | Steam turbine power plant | Hydro power plant | Gas turbine power plant | Nuclear power plant | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | Based on the Philippine Distribution Code, all users of the distribution system must maintain a certain power factor at the connection point in order to maintain power quality in the system. What power factor should be maintained at the connection point? | Not less than 65% | Not less than 70% | Not less than 85% | Not less than 75% | C
Fund. of Power Plant Engineering Design and Distribution and Substation Design | Objective | Which of the following is NOT considered in the selection of surge arrester? | Voltage rating | Current rating | Class of Arrester | Insulation level | D
Fund. of Power Plant Engineering Design and Distribution and Substation Design

## Power System Anal
Topic | Description | Question Text | Option A | Option B | Option C | Option D | Correct Answer
Power System and Analysis | Computation | A single-phase transmission lie is 30 km long, consists of two solid round conductor each of 1 cm in diameter. If the conductor spacing is 2.5 m, calculate the inductance per conductor. | 36 mH | 39 mH | 46 mH | 35 mH | B
Power System and Analysis | Computation | A single-phase transmission lie is 30 km long, consists of two solid round conductor each of 1 cm in diameter. If the conductor spacing is 2.5 m, calculate the total inductance of the loop. | 72 mH | 78 mH | 92 mH | 70 mH | B
Power System and Analysis | Computation | A three phase circuit, 60 Hz, 230 kV transposed line is composed of two 1272 MCM, 54/19 conductors per phase with horizontal configuration. The bundle spacing is 50 cm while spacing between the centers of the bundle is 10 m. If the GMR of the ACSR conductors is 0.0466 ft, what is the inductive reactance in ohm/km/phase of the transmission line? | 0.3775 | 0.3344 | 0.3969 | 0.3888 | A
Power System and Analysis | Computation | A 3-phase transmission line has three ACSR bundled conductors with 45 cm spacing between bundle centers are 9m, 9m and 18 m respectively. Find the inductance per km per phase. (GMR = 0.01176 m) | 1.03 | 0.98 | 0.888 | 1.223 | C
Power System and Analysis | Computation | The conductor of a transmission line are arranged in the form of equilateral triangle with sides of 6m each. If the conductor are 500 mils in diameter. What is its capacitive reactance in ohm-mile? | 203, 105 | 178897 | 134, 566 | 128, 667 | A
Power System and Analysis | Computation | Three-phase line is composed of 1272 MCM ACSR. The conductor is 7.6m, 7.6 m, and 12.8 m apart. The conductors have a diameter of 1.345 inches. Find the capacitance in micro-Farad per km. | 0.0058 | 0.0089 | 0.0072 | 0.0066 | B
Power System and Analysis | Computation | An overhead single-phase transmission line delivers 1 100 kW at 33 kV, 0.8 lagging pf. The resistance of the line is 10 ohms and total inductive reactance is 15 ohms. Determine the sending end pf. | 0.759 lagging | 0.795 leading | 0.759 leading | 0.795 lagging | D
Power System and Analysis | Computation | A short transmission line with an impedance of 5 + j6 ohms is supplying balanced load at receiving end voltage of 13.2 kV. Under this condition, the voltage regulation is at 8%. Calculate the sending end voltage. | 13.8 kV | 13.5 kV | 14.3 kV | 15.2 kV | C
Power System and Analysis | Computation | In a short three – phase transmission line, the receiving end line voltage is 240 V rms and the impedance of the line is 0.1 + j0.2 ohms. Requires 15 kW at the receiving end and the losses is 660 W. What is the phase voltage of the line? | 138 + j16 | 136 +j18 | 157.5 + j20 | 148.2+j4.2 | D
Power System and Analysis | Computation | The sending and receiving end voltage of a three-phase short transmission line are 33 kV and 31.2 kV, respectively. The per phase line parameters are R = 10 ohms an inductive reactance of 20 ohm. Calculate the maximum power that can be delivered by the line. | 26.57 MW | 7.67 MW | 100 MW | 32.54 MW | A
Power System and Analysis | Computation | A short 3-phase, 3 wire, 230 kV, transmission line has an impedance of 5 cis 78. The sending power is 150 MW, 230 kV, 85% pf lagging. What is the %VR of the line? | 1.16% | -1.16% | 3.64% | -3.64% | A
Power System and Analysis | Computation | A 230 kV transmission line is sending 100 MW power at 230 kV and 90% power factor. The impedance is 5 + j20 ohms and its capacitive reactance is – j2500 ohms. Determine the receiving end voltage. | 221.72 kV | 222.83 kV | 226.15 kV | 224.28 kV | B
Power System and Analysis | Computation | A 3 phase, 60 Hz transmission line delivers 20 MVA to a load at 66 kV at 80% pf lagging. The total series impedance of each line is 15 + j75 ohms. If a nominal pi circuit is used, what would be the transmission efficiency if the admittance is j0.0006 siemens? | 90.8% | 91.7% | 93.5% | 92.62% | D
Power System and Analysis | Computation | A short 230 kV transmission line has an impedance of 10 cis80. The sending end power is 150 MW at 230 kV and 82% pf. What is the voltage at the other end? | 222.45 kV | 223.45 kV | 224.45 kV | 225.45 kV | C
Power System and Analysis | Computation | The conductor of a three phase transmission line are arrange in the form of an equilateral with sides of 6 m each. If the conductors are 500 mils in diameter and the line is 25 km long, what is the inductance per phase? | 35.5 mH | 3.55 mH | 71 mH | 7.1 mH | A
Power System and Analysis | Computation | A 69 kV three – phase transposed line is composed of one ACSR 336, 400 cmil, 26/7 linnet conductor per phase with a horizontal configuration of D12 = 5 ft, D23 = 5 ft, D13 = 10 ft. The conductor have a diameter of 0.721 inch and a GMR of 0.0243 ft. Find the inductance of phase per km of the line. | 1.1116 mH/km | 1.0963 mH/km | 1.1505 mH/km | 1.1233 mH/km | D
Power System and Analysis | Computation | An ACSR conductor has an (n-1) layers around its single center strand, the total number of strands will be | 3n^2 + 3n + 1 | 3n^2 -3n -1 | 3n^2 + 3n -1 | 3n^2 -3n + 1 | D
Power System and Analysis | Computation | A single phase, 10 km transmission line has a 16.65 mH total inductance. If the distance between the conductors is 1 m, what is the conductor radius? | 2 cm | 1.5 cm | 1 cm | 0.75 cm | A
Power System and Analysis | Computation | A single phase transmission line having a length of 15 miles is composed of two copper conductors spaced 7 ft apart having a diameter of 0.575 inch. Determine the line to line capacitance in Farad if the system frequency is 60Hz. | 4.9 picoFarad | 9.8 picoFarad | 11.8 nanoFarad | 118 nanoFarad | D
Power System and Analysis | Computation | A 3 phase transmission line has two aluminum conductors in bundle. The self GMD of each conductor is 8.90 mm and the distance between the conductors and phases is 40 cm and 9 m, respectively. What is the inductance of line per phase in microHenry/m? | 1 | 2 | 3 | 4 | A
Power System and Analysis | Objective | Which of the following is a type of substation? | Gas Insulated Substation | Air Insulated Substation | Hybrid Substation | All of the above | D
Power System and Analysis | Objective | In substation, current transformers are used to _______. | Measuring Purpose | Protection purpose connection to relays | Both (A) & (B) | none of the above | C
Power System and Analysis | Objective | What is IEEE 21? | Ground Distance Relay | Phase Distance Relay | Overvoltage Relay | Recloser Switch | B
Power System and Analysis | Objective | Interrupting medium in a contactor may be ____________. | Air | SF6 gas | Oil | All of the above | D
Power System and Analysis | Objective | Air used in air – blast circuit breaker ___________. | must have atleast carbon dioxide | must be ionized | must be free from moisture | must be oil mist | C
Power System and Analysis | Objective | In a circuit breaker, the time duration from the instant of fault to the instant of closing of contact is known as __________. | recycle time | total time | gross time | reclosing time | D
Power System and Analysis | Objective | In a circuit breaker, the time duration from the instant of fault to the instant of extinction of arc is known as _______. | operation time | total clearing time | lead time | lag time | B
Power System and Analysis | Objective | In long transmission line, at no load, the receiving end voltage as compared to the sending end voltage is ______. I.Higher II. Lower III. Remains the same | I only | II only | Either 1 or II | III only | A
Power System and Analysis | Objective | If the effect of earth is taken into account, then the capacitance of line to ground | decreases | increases | remains unchanged | becomes infinite | B
Power System and Analysis | Objective | Which of the following type of fault that used only the equivalent positive impedance of the circuit in the short circuit analysis calculation? | line to line fault | Double line to ground fault | Three phase fault | Single line to ground fault | C
Power System and Analysis | Objective | Which of the following parameters can be neglected for a short line? | resistance | inductance | reactance | capacitance | C
Power System and Analysis | Objective | Which of the following insulators will be selection for high voltage application? | Strain Type | Disc Type | Suspension Type | Pin Type | C
Power System and Analysis | Objective | If the effect of earth is taken into account, then the capacitance of the line to ground. | decrease | increase | remain unchanged | becomes infinite | B
Power System and Analysis | Objective | The effective resistance of the conductor is increased by | skin effect | proximity effect | corona effect | both (A) and (B) | D
Power System and Analysis | Objective | Surge impedance of transmission line is given by | sq.rt. of C/L | sq.rt of LC | 1/sq.rt of LC | sq.rt of L/C | D
Power System and Analysis | Objective | A two terminal pair of network of a transmission line can be represented by a | pi-network | T-network | either (A) or (B) | tree network | C
Power System and Analysis | Objective | The effect of corona is | increase reactance | increase inductance | increase energy loss | all of these | C
Power System and Analysis | Objective | In a transmission line of negligible resistance, the surge impedance will be____________ | square root of LC | square root of L/C | 27 | 51 | B
Power System and Analysis | Objective | What is the purpose of reactor in short circuit? | To open the line in short circuit | To decrease the circuit resistance | To lessen the current in short circuit | To increase the current in short circuit | C
Power System and Analysis | Objective | For constant transmission efficiency, voltage is increased n times, the size of the conductor would be ______________ | Reduced to (1/n) times of the original | Reduced to (1/n^2) times of the original | Increased to n^2 times of the original | Increased to n times of the original | A
Power System and Analysis | Objective | The power transmission capacity of the transmission is________________ | Inversely proportional too voltage | Directly proportional to voltage | proportional to the square of voltage | proportional to the cube of the voltage | C
Power System and Analysis | Objective | Which of the following type of fault used only the equivalent positive sequence impedance of the circuit in the short circuit calculation? | line to line | line to ground | double line to ground | three-phase fault | D
Power System and Analysis | Objective | Which of the following that the voltage regulation is one of the important factors consider in the electrical power design? | generator | transmission line | feeder | transformer | B
Power System and Analysis | Objective | Which of the following type of fault used only the equivalent positive and negative sequence impedance of the circuit in the short-circuit calculation? | double line to ground | line to line | three-phase | line to ground | B
Power System and Analysis | Objective | For a transmission line with resistance R Ω, reactance X Ω and negligible capacitance, the parameter A is | 0 | R + jX | 1 | (R² + X²)^1/2 | B
Power System and Analysis | Objective | The efficiency of transmission increases as | system voltage and load power factor both decreases | system voltage and load power factor both increase | system voltage decreases but load power factor increases | system voltage increases but load power factor decreases | B
Power System and Analysis | Objective | Bundled conductors in EHV transmission system provide | reduced capacitance | increased voltage gradient | increased capacitance | increased inductance | C
Power System and Analysis | Objective | Whenever the conductors are dead ended or there is a change in the direction of transmission line, the insulators used are of the | pin type | suspension type | strain type | shackle type | C
Power System and Analysis | Objective | The voltage regulation of a long EHV transmission line at no load is | negative | positive | zero | unity | A
Power System and Analysis | Objective | The alternate layers of an ACSR conductor are spiraled in opposite direction to | prevent unwinding | increase capacitance | reduce inductance | make it mechanically stronger | C
Power System and Analysis | Objective | Corona loss increases with | increase in supply frequency and conductor size | increase in supply frequency and reduction in conductor size | decrease in supply frequency and reduction in conductor size | decrease in supply frequency and increase in conductor size | A
Power System and Analysis | Objective | The electrostatic stress in a single-core belted cable is | minimum at the conductor surface and maximum at the sheath | maximum at the conductor surface and minimum at the sheath | same throughout the insulation thickness | maximum both at the conductor surface and at the sheath and minimum at the armoring layer. | B
Power System and Analysis | Objective | A stringing chart is useful | in the location of transmission towers | in the determination of number of units in a string of insulators | in finding the sag at different temperature | for checking uplift force on towers | C
Power System and Analysis | Objective | The fact that a conductor carries more current on the surface as compared to core, is known as | skin effect | corona | permeability | unsymmetrical fault | A
Power System and Analysis | Objective | Presence of ozone as a result of corona is harmful because | it gives bad odor | it corrodes the material | it transfers energy to the ground | reduces power factor | A
Power System and Analysis | Objective | In transmission line having negligible resistance, the surge impedance is | √{L + C} | √{C / L} | 1 / √{CL} | √{L / C} | D
Power System and Analysis | Objective | The function of steel wire in an ACSR conductor is | to take care of surges | to prevent corona | to reduce inductance | to provide additional mechanical strength | D
Power System and Analysis | Objective | For a transmission line with negligible losses, the lagging reactive power (VAR) delivered at the receiving-end, for a given receiving-end voltage is directly proportional to the | square of the line voltage drop | line voltage drop | line inductance reactance | line capacitive reactance | D
Power System and Analysis | Objective | A 30 km transmission line carrying power at 33 kV is known as | short transmission line | long transmission line | high power line | ultra high voltage line | A
Power System and Analysis | Objective | 750 kV is termed as | medium high voltage | high voltage | extra high voltage | ultra high voltage | C
Power System and Analysis | Objective | The sag of a transmission line is least affected by | self weight of conductors | temperature of surrounding air | current through conductor | ice deposited on conductor | C
Power System and Analysis | Objective | In EHV transmission lines, efficiency of transmission can be increased by decreasing the corona loss. This is achieved by | increasing the distance between the line conductors | using bundled conductors | using thick conductors | using thin conductors | B